## Slide 1: Treatment – Chemical Filters
Matt Bower
DWQR Risk Assessment Training
2018

## Slide 2: Overview 1
Act chemically via adsorption rather than physically
Chemicals “stick” to media
Media gradually exhausts leading to breakthrough
Some media can be regenerated, others single use
Mostly loose media filters but some cartridge
Expensive process needing careful monitoring

## Slide 3: Overview 2
Types of Chemical Filtration Media
Granular Activated Carbon (GAC)
Manganese Dioxide (“Polarite”, Greensand)
Most Common
Organic compounds
Colour
Range of types with different properties
Other Media – clays, minerals, glass
Catalyses removal of soluble manganese
Activated Alumina
A number of metals and arsenic
Effective, but highly pH sensitive
Ferric Oxides / Hydroxides
Arsenic and many other metals
Regeneration may be possible

## Slide 4: Usage 1
Remember – these are chemical filters
Water needs to be clean first
Backwash to gently expand bed
Carefully monitor for breakthrough and plan for replacement
Ensure adequately sized for flow
Dispose of spent media carefully
Specialist advice….

## Slide 5: Usage 2
Cartridge Adsorption
Smaller scale GAC filters
Commonly used for colour
Single use
Could exhaust very quickly
Needs pre-treatment

## Slide 6: Key Points to Watch For 1
Good design would be….
Pre-treatment
Flow monitoring
Backwash system (not too vigorous!)
Instruction manual + specification
Sample points
Multiple units in parallel

## Slide 7: Key Points to Watch For 2
Good operation would be….
Flows evenly split
Replace all media in vessel, not top up
Automatic / regular monitoring of parameter(s) being removed
Plans for regular media replacement
Inlet and outlet for breakthrough or increased contamination
Records kept

## Slide 8: Questions
Class | Treatment | Code | Question | Notes | Risk Score
Management and Resilience | Treatment | TCR1 | Could raw water quality exceed the filter design parameters, leading to contaminant breakthrough? | If raw water quality varies significantly beyond the design parameters for the filter, there is a risk that the filter may not perform effectively. Some waters can deteriorate significantly in quality after heavy rainfall. | 4
Management and Resilience | Treatment | TCR2 | Could inadequate / loss of media cause quality problems? | Filters should be correctly sized and periodically inspected to ensure that there is sufficient media in place to adequately remove contaminants from the water. The physical quality of media can deteriorate over time (as well as it becoming chemically exhausted) | 4
Management and Resilience | Treatment | TCR3 | Could the maintenance regime for the filter be inadequate or undocumented? | Filters require maintenance to ensure on-going performance. This needs to be performed at the correct frequency and should be recorded consistently. | 4
Installation and Operation | Treatment | TCR4 | Could inadequate or no backwash facility cause filter failure? | All filters containing loose media require backwashing to ensure continued operation. For GAC filters the purpose of backwashing is to expand the filter bed and prevent compaction. | 4
Management and Resilience | Treatment | TCR5 | Could the programme of monitoring and replacement of filter media on exhaustion be insufficient to prevent contaminant breakthrough? | GAC is a chemical filter and will eventually become exhausted. The rate of exhaustion will depend upon the amount of colour or other contaminants in the water and the flow rate through the filter. This breakthrough is difficult to predict, hence careful monitoring is required. | 4
Microbiological | Treatment | TCR6 | Could microbiological activity on the filter compromise quality? | GAC provides a good support media for microbiological growth. If this is not controlled properly this can cause problems. Consequently any disinfection process should be downstream of GAC filters. | 4