## Slide 1: Treatment – Slow Sand Filters
Matt Bower
DWQR Risk Assessment Training
2018

## Slide 2: Overview
One of oldest forms of water treatment
Unlikely to see on PWS
Can be effective at treating water to high standard, both chemically and microbiologically
Needs regular monitoring and maintenance
Large, shallow, biologically active filters

## Slide 3: Usage
Good for surface waters where microbiology and algae can be a problem
Could work on a smaller scale – never seen
Biologically active layer called schmutzdecke develops on surface
Needs “skimming” every few weeks then period of ripening
No chemical usage – nature does the work
Best to operate two in tandem

## Slide 4: Key Points to Watch For
Is water flowing onto filter of suitable quality (Turbidity consistently <10NTU)?
Suitable disinfection process needed downstream
Is suitable period allowed for ripening (few weeks)?
Filter needs to be open to environment
Is there a maintenance plan for skimming?

## Slide 5: Questions
Type | Treatment | Code | Question | Notes | Risk Score
Management and Resilience | Treatment | TSS1 | Could filter media composition deviate from design specification? | The type of sand to be used should be specified. | 5
Management and Resilience | Treatment | TSS2 | Could media depth deviate from minimum design specification? | The depth of media should be specified. | 5
Installation and Operation | Treatment | TSS3 | Could ripening period for the slow sand filters prior to putting water into supply be inadequate or ignored? | Slow sand filters rely on a biological process that requires a ripening period before the bed is ready to perform effectively. This period should be documented on site and accounted for following any media replacement or skimming. | 5
Installation and Operation | Treatment | TSS4 | Is maintainance of filters (including regular skimming) inadequate for effective operation of filters? | Slow sand filters need periodic maintenance in order to perform effectively. This should include monitoring of the surface of the bed to ensure that biological growth does not become excessive, choking the filter. Periodic skimming will be needed to maintain performance, and the required frequency should be documented on site. | 5