## Slide 1: Treatment – Plant Design
Matt Bower
DWQR Risk Assessment Training
2018

## Slide 2: Process Design Part 1
Take a step back – see the big picture
Consider raw water quality
What is water used for?
Where does the water need to go?
Emerging risks
Is there enough information?

## Slide 3: Process Design Part 2
Ask Yourself a Few Questions
How would I design the treatment process from scratch?
What could go wrong?
Where does the water need to go?
Is it dealing with all water quality issues
Is everything that is here necessary?
Is there anything here that isn’t needed?
Regulated and unregulated (Crypto)

## Slide 4: Capacity & Flow
What is the max water flow through the process?
Some process are sized for a certain flow
Is the process reliant on blending out contaminants?
How variable is the flow?
UV
Chemical filters
Is flow measured anywhere?
Can the process cope with that (chemical dosing needs to adjust)
This needs to be controlled and monitored
Is there a flow “pinch point”?

## Slide 5: Quality
How is it being monitored?
Some processes need stable quality; others will only work within certain parameters
Some parameters / process need regular checks
How does it change over time?
Chemical dosing
Chemical filters

## Slide 6: Installation
Stuff only works when it is fitted correctly……
In line with manufacturers’ specifications / guidance?
Should be installed with maintenance in mind
Follow the process - does it look logical to you?
Competent installer?
Pitfalls – Bypasses, Short-circuiting, Contamination

## Slide 7: Records and Information Part 1
Ideally…..
A schematic diagram of whole treatment process
Validation information / certification
We’ll come back to this subject in MANAGEMENT CONTROL……..
Operating manual for each process
Required maintenance
Parts
Chemical specifications

## Slide 8: Records and Information Part 2

## Slide 9: Questions Part 1
Code | Question | Notes | Risk Score
TPD1 | Is the treatment process layout inadequately documented? | A treatment plan or schematic should be available, this can be a simple sketch or a more complex and detailed drawing depending on the scale of the treatment. This should at least include locations of the incoming water flow, direction of flow, bypass points, dosing points, treatment type and points, monitor locations, out flow, etc. and materials. It need not be to scale but should represent the main treatment of the supply. | 5
TPD2 | Has there been inadequate consideration of Cryptosporidium in design of treatment? | Cryptosporidium is found in faecal matter from livestock and wildlife and in sewage. It can affect any surface water sources or vulnerable ground water sources influenced by surface water. A multi-barrier approach is recommended to remove Cryptosporidium from supplies; coagulation, clarification and filtration for example. Chlorination is not effective against Cryptosporidium, however, UV treatment will inactivate it. | 5
TPD3 | Is the treatment plant operating outside its design capacity? | For any treatment process, there are operational limits beyond which treatment performance diminishes. The quality of the drinking water being produced may be adversely affected if this occurs. Therefore any process being used beyond its designed capacity or specification requires action to be taken. Refer to any available information provided by the manufacturer on the design specification for the treatment and criteria on which the treatment process was designed. Check whether the 'demand' on the supply has significantly increased since the plant was designed and built, e.g. from additional commercial premises, large numbers of additional houses. Check the volume of water being treated and the type of treatment process. Flows greater than design capacity will compromise water quality, e.g. due to insufficient contact time with UV or overloading of filters. | 5
TPD4 | Is there a lack of knowledge and documentation on the treatment plant design / capability / capacity? | It is essential to have a knowledge of the treatment so that any problems can be identified and appropriate mitigation action taken. If an understanding of the treatment of the supply is not demonstrated and no maintenance contract is in place, then the likelihood should be scored as 5. Manuals or manufacturer's instructions for the treatment should be available at the site. | 5
TPD5 | Is it possible to by-pass any stage of treatment? | Check for pipe work and/or valves that by-pass any treatment stage. If a UV lamp can be easily switched off (e.g. to save electricity) this is bypassing a treatment stage. | 5

## Slide 10: Questions Part 2
Code | Question | Notes | Risk Score
TPD5 | Is it possible to by-pass any stage of treatment? | Check for pipe work and/or valves that by-pass any treatment stage. If a UV lamp can be easily switched off (e.g. to save electricity) this is bypassing a treatment stage. | 5
TPD6 | Where there is a blending facility, is the blending strategy inappropriate? | Blending can be the mixing of a public water supply with a private supply or between multiple private water sources. This may be carried out to meet water quality standards. Assessment of the blending strategy requires interpretation of sample results and knowledge of seasonal variations, e.g. of boron, arsenic, fluoride and nitrates. Check that procedures are in place for the calculation and management of the blending ratio. I.e. are the sources being blended in the correct quantities to meet the criteria defined in procedures to eliminate exceedances of the standards? Does the strategy take into account seasonal variations? | 4
TPD7 | Are there frequent flow/demand variations through the treatment plant, which render the treatment process inadequate in terms of either sufficiency or quality? | Variations in flow rates can cause low pressure, insufficient or loss of supply to properties. Flow variations may also compromise water quality by affecting coagulation, clarification, filtration and disinfection treatment processes, particularly when sudden changes occur. Changes to flow rates should therefore be made gradually and should not exceed the design capacity of any individual treatment process. | 4
TPD8 | Are there large raw water quality variations, which could exceed the design capability of the treatment process ? | Some treatment processes struggle to cope with rapid changes in the quality of the water they are required to treat. If this is the case it may be necessary to install pre-treatment or storage in order to ensure a more consistent quality of water entering the main treatment process. | 4
TPD9 | Does / could inadequate installation cause quality problems? | Potentially effective treatment processes can be rendered less effective by innappropriate installation, in terms of siting and the way in which they are connected or commissioned. Check for obvious issues such as short circuiting and post-treatment contamination. Treatment equipment should come with detailed installation instructions and / or be fitted by a trained person. | 5