## Slide 1: Introduction
Is Radon in Groundwater Dangerous?
Who am I?
Who are HighWater?
Background to this study

## Slide 2: Is Radon in Groundwater Dangerous?
David Hine (General Manager, HighWater)
Robert Kerr (HighWater’s retained Radiological Protection Adviser)
Warren Bradshaw (formerly Highland Council)
Michael Ayres (Managing Director, HighWater)

## Slide 3: Is Radon in Groundwater Dangerous? 1
Uranium decay series > Radon & progeny
Radon Map
Radon and the PWS Regs
Radon in air
Risk Assessment
Mitigation
Summary

## Slide 4: Is Radon in Groundwater Dangerous?
Gas at room temperature
Colourless
Odourless
Tasteless
Very dense compared to air
Half life of 3.8 days
Dangerous daughters!

## Slide 5: Is Radon in Groundwater Dangerous? 2

## Slide 6: WIFHC 2017 Regs
Is Radon in Groundwater Dangerous?
Parametric Value 100Bq/l (PCV)
Threshold Value 1000Bq/l

## Slide 7: Is Radon in Groundwater Dangerous? 3
Ra
Ra
Ra
2.5m
2m
2m
1,000l ground water containing 100Bq/l pumped into storage tank
Assuming all radon gas escapes from water
1,000l X 100Bq/l = 100,000Bq of Radon in the Shed
Shed volume is 10m³
Therefore 10,000Bq/m³ in the shed
The Action Limit is 300Bq/m³
This is over 32 times the limit!

## Slide 8: Existing Literature
Is Radon in Groundwater Dangerous?
DWQR “Radon – Guidance for Local Authorities”
Water UK “Radon in air – Occasional guidance note”

## Slide 9: Risk Assessment (IRR 97)
Is Radon in Groundwater Dangerous?
28 high risk sites identified
9 exceeded 300Bq/m3 (highest 24,000Bq/m3)
Considered staff by role & duration
Worst case 0.39 milliSv (limit 1 milliSv)

## Slide 10: Mitigation - Design Considerations
Is Radon in Groundwater Dangerous?
Passive Venting
External tank overflow
Sealed lids

## Slide 11: Mitigation – Working Practices
Is Radon in Groundwater Dangerous?
Extractors
Wait!
Leave doors open

## Slide 12: Mitigation - Treatment
Is Radon in Groundwater Dangerous?
Avoid adsorption media such as Activated Carbon or Bonechar due to NORM accumulation

## Slide 13: Summary
Is Radon in Groundwater Dangerous?
Radon in groundwater is not a problem…
…and thankfully Radon in air is a manageable problem!
Q & A