## Slide 1: Treatment – Sediment Filters
Matt Bower
DWQR Risk Assessment Training
2018

## Slide 2: Overview
Filters containing loose media, housed in a plastic or metal shell
Usually (but not always) for larger PWS
Often contain sand, but may contain other inert or catalytic media
May be used to removal metals (perhaps with oxidation stage)
Point of Entry or Common treatment systems

## Slide 3: Usage
Sealed Units – operate under pressure
May be installed in series or parallel
Usually downflow; need backwashing to avoid bed compaction and clogging
Sometimes have automatic backwash timer fitted on top
Should be sited where there is room to access for inspection and maintenance

## Slide 4: Usage Part 1
Metals removal
Iron, Manganese, Chromium (III), Selenium, Arsenic (III)
Aeration is easiest – air sparge pipe; cascade
Some metals (Mn) may require chemical oxidation (Cl) or raising pH
Thought on design needed (want metal to precipitate on filter!)
May be desirable to have detention (settlement tank) upstream to allow precipitation
Usually need to oxidise metal to make it insoluble

## Slide 5: Usage Part 2
Backwashing
Needed to expand bed and wash off deposits
Flow and frequency needs to be set to according to usage (watch until B/W water runs clear)
Ideally use automatic timed system
Backwashing problems
Can use mixture of air and / or water
Lack of sufficient clean water
Starving system of water during B/W
Disposal of B/W water
Insufficient flow / time / frequency

## Slide 6: Key Points to Watch For
Are we clear what filter is there to do (solids, metals, chemicals)?
Is there any media inside it?!
Is any pre-oxidation sufficient?
What is the backwash regime? Is it enough? Is it monitored?
Maintenance (media, moving parts)
Is it sufficiently sized?

## Slide 7: Questions
Type | Treatment | Code | Question | Notes | Risk Score
Management and Resilience | Treatment | TSF1 | Could soluble metals be present due to inadequate pre-oxidation (if process requires it - Fe / Mn)? | Filtration may be preceded by pre-oxidation dependent on the solubility of the metals in the source water and corresponding design of the treatment works. Pre-oxidation brings the metals out of solution so that they can be removed through the filter from the raw water. Evidence of the requirement for pre-treatment or of inadequate pre-treatment is raised levels of metals in the filtered water. | 5
Installation and Operation | Treatment | TSF2 | Could process issues across filters go undetected? (e.g. are there turbidity or head loss monitors?) | Filter performance may be determined using turbidity monitors - ideally on the outlet of each filter. Where filtered water turbidity is higher than 1.0NTU or where this value is frequently approached then action is needed to improve filter performance and/or any preceding treatment processes. A typical filter cycle will show increased turbidity at the start and end of the cycle (after commissioning and prior to backwashing or refurbishment); these are normal and should be managed operationally. Where there are no turbidity monitors or metal levels are not routinely checked then process issues with filters may go undetected. | 5
Management and Resilience | Treatment | TSF3 | Do the filters block/overload? | Confirm whether the operator checks the filters, e.g. the surface should appear an even colour, they should be monitored for headloss and turbidity. Determine the regularity of these checks, and of backwashes and media replacement. Check that the filters are managed so they cannot overload; the number of filters should be appropriate to the volume of water being processed. The operator should ensure that the incoming water is evenly distributed across all filters. | 5
Management and Resilience | Treatment | TSF4 | Is there a risk of poor or no maintenance? | Although fairly trouble-free, all filters need maintenance to ensure that they continue to operate effectively. Any automatic backwash mechanisms should be checked and serviced in accordance with manufacturer's guidelines. Valves should be checked to ensure they remain operable. The media in the filter should be inspected periodically to check that it is in good condition and there is sufficient to enable the filter to perform effectively. | 4
Management and Resilience | Treatment | TSF5 | is there a risk that instructions for the filter operation and maintenance are undocumented? | All filters should be operated in accordance with manufacturers' instructions. If these are not present, there is a risk that the performance of the filter could be compromised due to inappropriate operation or inadequate maintenance. | 5

## Slide 8: Questions Part 2
Type | Treatment | Code | Question | Notes | Risk Score
Installation and Operation | Treatment | TSF6 | Is there evidence that backwashing is inadequate? | Most filters are designed to be backwashed periodically to clean the media and remove dirt and sediment that has accumulated on the surface of the bed. Poor washing can greatly reduce the effectiveness of filtration. Sometimes the design of the filter can be the cause of inadequate backwashing, in other cases it is due to deficiencies with the operation and maintenance of the filter. An effective backwash should expand the media bed and have sufficient vigour to lift particulate matter and remove it via the waste stream. The timings for the wash should be set so that the washwater is running clear by the time the backwash ends. | 5
Installation and Operation | Treatment | TSF7 | Could dirty water left in the filter or pipework enter the supply when filters first start up (e.g. does it run to waste?) | Dirty backwash water can contain harmful pathogens. During the period when a filter is returned to service immediately after a backwash there is an increased risk that dirty water will enter the supply. A "run to waste" or "slow start" mechanism can reduce this risk. With the design of some filters, dirty washwater that remains in pipework after the wash can enter supply once normal flow is re-started. | 5
Management and Resilience | Treatment | TSF8 | Could inadequate / loss of media cause quality problems? | Any filter needs sufficient media in order to perform effectively. The media in the filter should be inspected periodically to check the amount of media. Media should be topped up if necessary. | 4
Management and Resilience | Treatment | TSF9 | Could backwash water be inappropriately disposed of and become a risk to quality? | Dirty Backwash water can contain harmful pathogens. It should be disposed of in a manner that prevents it re-entering the treated water stream or causing contamination elsewhere. | 5